## Pressure Loss Curves
Number | Type | Entry Section Sub-type | Cross-sectional Area | Entry Geometry | Number of inlets | Filter | N_filter | a2 | a1 | a0
I1 | Inlet | Front | Standard | Concealed | Single | G4 | 3.5 | 0.00043117 | 0.21778 | -4.3294
I2 | Inlet | Front | Standard | Concealed | Triple | G4 | 3.5 | 0.0004575 | 0.19899 | -0.35482
I2 | Inlet | Cup | Standard | Concealed | Triple | G4 | 3.5 | 0.015148 | 0.84394 | 1.9692
I3 | Inlet | Front | Standard | Concealed | Single | G3 | 3.5 | 0.0003203 | 0.065787 | 7.1203
I4 | Inlet | Front | Standard | Concealed | Triple | G3 | 3.5 | 0.00048027 | -0.059271 | 32.5097
I4 | Inlet | Cup | Standard | Concealed | Triple | G3 | 3.5 | 0.008403 | 0.20779 | 22.1172
I5 | Inlet | Front | Standard | Grille | Single | G4 | 3.5 | 0.00036611 | 0.1911 | 7.1744
I6 | Inlet | Front | Standard | Grille | Triple | G4 | 3.5 | 0.00051647 | 0.077373 | 29.5615
I6 | Inlet | Cup | Standard | Grille | Triple | G4 | 3.5 | 0.015148 | 0.84394 | 1.9692
I7 | Inlet | Front | Standard | Grille | Single | G3 | 3.5 | 0.00023817 | 0.059061 | 7.0179
I8 | Inlet | Front | Standard | Grille | Triple | G3 | 3.5 | 0.0003915 | -0.058238 | 30.4968
I8 | Inlet | Cup | Standard | Grille | Triple | G3 | 3.5 | 0.008403 | 0.20779 | 22.1172
I1 | Inlet | Front | Standard | Concealed | Single | G4 | 1 | 0.00027333 | 0.066214 | 7.3395
I2 | Inlet | Front | Standard | Concealed | Triple | G4 | 1 | 0.00043044 | -0.055112 | 31.5468
I2 | Inlet | Cup | Standard | Concealed | Triple | G4 | 1 | 0.0073882 | 0.22472 | 21.5406
I3 | Inlet | Front | Standard | Concealed | Single | G3 | 1 | 0.00023678 | 0.02849 | 7.2948
I4 | Inlet | Front | Standard | Concealed | Triple | G3 | 1 | 0.00039473 | -0.093858 | 31.8141
I4 | Inlet | Cup | Standard | Concealed | Triple | G3 | 1 | 0.0066 | 0.0769 | 21.717
I5 | Inlet | Front | Standard | Grille | Single | G4 | 1 | 0.0001912 | 0.059488 | 7.2371
I6 | Inlet | Front | Standard | Grille | Triple | G4 | 1 | 0.00034167 | -0.054079 | 29.534
I6 | Inlet | Cup | Standard | Grille | Triple | G4 | 1 | 0.0073882 | 0.22472 | 21.5406
I7 | Inlet | Front | Standard | Grille | Single | G3 | 1 | 0.00015465 | 0.021764 | 7.1924
I8 | Inlet | Front | Standard | Grille | Triple | G3 | 1 | 0.00030597 | -0.092825 | 29.8012
I8 | Inlet | Cup | Standard | Grille | Triple | G3 | 1 | 0.0065725 | 0.076861 | 21.7172
O1 | Outlet | Back | Standard | Concealed | Single | G4 | 3.5 | 0.00043117 | 0.21778 | -4.3294
O2 | Outlet | Back | Standard | Concealed | Single | G3 | 3.5 | 0.0003203 | 0.065787 | 7.1203
O3 | Outlet | Back | Increased 01 | Concealed | Single | G4 | 3.5 | 0.0003 | 0.1564 | 2.9753
O4 | Outlet | Back | Increased 01 | Concealed | Single | G3 | 3.5 | 0.0003 | 0.0344 | 4.7606
O5 | Outlet | Back | Standard | Grille | Single | G4 | 3.5 | 0.00036611 | 0.1911 | 7.1744
O6 | Outlet | Back | Standard | Grille | Single | G3 | 3.5 | 0.00023817 | 0.059061 | 7.0179
O7 | Outlet | Back | Increased 01 | Grille | Single | G4 | 3.5 | 0.0002 | 0.1456 | 5.5894
O8 | Outlet | Back | Increased 01 | Grille | Single | G3 | 3.5 | 0.0002 | 0.0391 | 4.1146
O9 | Outlet | Back | Standard | Concealed | Single | G4 | 1 | 0.00027333 | 0.066214 | 7.3395
O2 | Outlet | Back | Standard | Concealed | Single | G3 | 1 | 0.00023678 | 0.02849 | 7.2948
O3 | Outlet | Back | Increased 01 | Concealed | Single | G4 | 1 | 0.0003 | 0.0145 | 11.192
O4 | Outlet | Back | Increased 01 | Concealed | Single | G3 | 1 | 0.0002 | 0.0005 | 5.1402
O5 | Outlet | Back | Standard | Grille | Single | G4 | 1 | 0.0001912 | 0.059488 | 7.2371
O6 | Outlet | Back | Standard | Grille | Single | G3 | 1 | 0.00015465 | 0.021764 | 7.1924
O7 | Outlet | Back | Increased 01 | Grille | Single | G4 | 1 | 0.0001 | 0.0356 | 4.9156
O8 | Outlet | Back | Increased 01 | Grille | Single | G3 | 1 | 0.0001 | 0.0052 | 4.4943

## Sheet1
[11 empty] | I1 | Single Inlet, G4 Filter |  | I2 | Triple Inlet, G4 Filter |  | I2 |  |  |  |  | I3 | Single Inlet, G3 Filter |  | I4 | Triple Inlet, G3 Filter |  | I4 |  |  |  |  | I5 | Single Inlet, G4 Filter, Grille |  | I6 | Triple Inlet, G4 Filter, Grille |  | I6 |  |  |  |  | I7 | Single Inlet, G3 Filter, Grille |  | I8 | Triple Inlet, G3 Filter, Grille |  | I8
| 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 0.00043117 | 0.21778 | -4.3294 | 0.0004575 | 0.19899 | -0.35482 | 0.015148 | 0.84394 | 1.9692 |  |  | 0.0003203 | 0.065787 | 7.1203 | 0.00048027 | -0.059271 | 32.5097 | 0.008403 | 0.20779 | 22.1172 |  |  | 0.00036611 | 0.1911 | 7.1744 | 0.00051647 | 0.077373 | 29.5615 | 0.015148 | 0.84394 | 1.9692 |  |  | 0.00023817 | 0.059061 | 7.0179 | 0.0003915 | -0.058238 | 30.4968 | 0.008403 | -0.058238 | 30.4968
Number | Type | Entry Section Sub-type | Cross-sectional Area | Entry Geometry | Number of inlets | Filter | N_filter | a2 | a1 | a0 | Flowrate - [m^3/h] | Static Pressure - [Pa] |  | Flowrate - [m^3/h] | Static Pressure - [Pa] |  | Flowrate - [m^3/h] | Static Pressure - [Pa] |  | Flowrate - [m^3/h] | Static Pressure - [Pa] | Flowrate - [m^3/h] | Static Pressure - [Pa] |  | Flowrate - [m^3/h] | Static Pressure - [Pa] |  | Flowrate - [m^3/h] | Static Pressure - [Pa] |  | Flowrate - [m^3/h] | Static Pressure - [Pa] | Flowrate - [m^3/h] | Static Pressure - [Pa] |  | Flowrate - [m^3/h] | Static Pressure - [Pa] |  | Flowrate - [m^3/h] | Static Pressure - [Pa] |  | Flowrate - [m^3/h] | Static Pressure - [Pa] | Flowrate - [m^3/h] | Static Pressure - [Pa] |  | Flowrate - [m^3/h] | Static Pressure - [Pa] |  | Flowrate - [m^3/h] | Static Pressure - [Pa] |  | Flowrate - [m^3/h] | Static Pressure - [Pa]
I1 | Inlet | Front | Standard | Concealed | Single | G4 | 3.5 | 0.00043117 | 0.21778 | -4.3294 | 700 | 359.3876 |  | 600 | 283.7395 |  | 50 | 82.0352 |  | 700 | 283.7395 | 700 | 210.1169 |  | 600 | 169.8428 |  | 50 | 53.5143 |  | 700 | 169.8428 | 700 | 320.3369 |  | 600 | 261.9139 |  | 50 | 82.0352 |  | 700 | 261.9139 | 700 | 165.0619 |  | 600 | 136.4935 |  | 50 | 48.5923 |  | 700 | 136.4935
I2 | Inlet | Front | Standard | Concealed | Triple | G4 | 3.5 | 0.0004575 | 0.19899 | -0.35482 | 710 | 367.6448 |  | 605 | 287.4909 |  | 52.5 | 88.0266 |  | 710 | 287.4909 | 710 | 215.291 |  | 605 | 172.4401 |  | 52.5 | 56.187 |  | 710 | 172.4401 | 710 | 327.4101 |  | 605 | 265.4124 |  | 52.5 | 88.0266 |  | 710 | 265.4124 | 710 | 169.0106 |  | 605 | 138.5611 |  | 52.5 | 50.6 |  | 710 | 138.5611
I2 | Inlet | Cup | Standard | Concealed | Triple | G4 | 3.5 | 0.015148 | 0.84394 | 1.9692 | 720 | 375.9883 |  | 610 | 291.2652 |  | 55 | 94.2074 |  | 720 | 291.2652 | 720 | 220.5291 |  | 610 | 175.0613 |  | 55 | 58.9648 |  | 720 | 175.0613 | 720 | 334.5565 |  | 610 | 268.9369 |  | 55 | 94.2074 |  | 720 | 268.9369 | 720 | 173.007 |  | 610 | 140.6483 |  | 55 | 52.7127 |  | 720 | 140.6483
I3 | Inlet | Front | Standard | Concealed | Single | G3 | 3.5 | 0.0003203 | 0.065787 | 7.1203 | 730 | 384.418 |  | 615 | 295.0624 |  | 57.5 | 100.5775 |  | 730 | 295.0624 | 730 | 225.8313 |  | 615 | 177.7066 |  | 57.5 | 61.8476 |  | 730 | 177.7066 | 730 | 341.7761 |  | 615 | 272.4871 |  | 57.5 | 100.5775 |  | 730 | 272.4871 | 730 | 177.051 |  | 615 | 142.755 |  | 57.5 | 54.9304 |  | 730 | 142.755
I4 | Inlet | Front | Standard | Concealed | Triple | G3 | 3.5 | 0.00048027 | -0.059271 | 32.5097 | 740 | 392.934 |  | 620 | 298.8824 |  | 60 | 107.137 |  | 740 | 298.8824 | 740 | 231.1976 |  | 620 | 180.3759 |  | 60 | 64.8355 |  | 740 | 180.3759 | 740 | 349.0689 |  | 620 | 276.0631 |  | 60 | 107.137 |  | 740 | 276.0631 | 740 | 181.1427 |  | 620 | 144.8813 |  | 60 | 57.2532 |  | 740 | 144.8813
I4 | Inlet | Cup | Standard | Concealed | Triple | G3 | 3.5 | 0.008403 | 0.20779 | 22.1172 | 750 | 401.5362 |  | 625 | 302.7253 |  | 62.5 | 113.8858 |  | 750 | 302.7253 | 750 | 236.6279 |  | 625 | 183.0692 |  | 62.5 | 67.9283 |  | 750 | 183.0692 | 750 | 356.435 |  | 625 | 279.665 |  | 62.5 | 113.8858 |  | 750 | 279.665 | 750 | 185.2819 |  | 625 | 147.0272 |  | 62.5 | 59.681 |  | 750 | 147.0272
I5 | Inlet | Front | Standard | Grille | Single | G4 | 3.5 | 0.00036611 | 0.1911 | 7.1744 | 760 | 410.2246 |  | 630 | 306.5911 |  | 65 | 120.824 |  | 760 | 306.5911 | 760 | 242.1222 |  | 630 | 185.7865 |  | 65 | 71.1263 |  | 760 | 185.7865 | 760 | 363.8742 |  | 630 | 283.2927 |  | 65 | 120.824 |  | 760 | 283.2927 | 760 | 189.4689 |  | 630 | 149.1927 |  | 65 | 62.2139 |  | 760 | 149.1927
I6 | Inlet | Front | Standard | Grille | Triple | G4 | 3.5 | 0.00051647 | 0.077373 | 29.5615 | 770 | 418.9993 |  | 635 | 310.4797 |  | 67.5 | 127.9515 |  | 770 | 310.4797 | 770 | 247.6806 |  | 635 | 188.5278 |  | 67.5 | 74.4292 |  | 770 | 188.5278 | 770 | 371.3867 |  | 635 | 286.9462 |  | 67.5 | 127.9515 |  | 770 | 286.9462 | 770 | 193.7034 |  | 635 | 151.3777 |  | 67.5 | 64.8517 |  | 770 | 151.3777
I6 | Inlet | Cup | Standard | Grille | Triple | G4 | 3.5 | 0.015148 | 0.84394 | 1.9692 | 780 | 427.8602 |  | 640 | 314.3912 |  | 70 | 135.2683 |  | 780 | 314.3912 | 780 | 253.3031 |  | 640 | 191.2932 |  | 70 | 77.8372 |  | 780 | 191.2932 | 780 | 378.9725 |  | 640 | 290.6256 |  | 70 | 135.2683 |  | 780 | 290.6256 | 780 | 197.9856 |  | 640 | 153.5824 |  | 70 | 67.5947 |  | 780 | 153.5824
I7 | Inlet | Front | Standard | Grille | Single | G3 | 3.5 | 0.00023817 | 0.059061 | 7.0179 | 790 | 436.8073 |  | 645 | 318.3256 |  | 72.5 | 142.7745 |  | 790 | 318.3256 | 790 | 258.9896 |  | 645 | 194.0825 |  | 72.5 | 81.3503 |  | 790 | 194.0825 | 790 | 386.6314 |  | 645 | 294.3308 |  | 72.5 | 142.7745 |  | 790 | 294.3308 | 790 | 202.3154 |  | 645 | 155.8065 |  | 72.5 | 70.4426 |  | 790 | 155.8065
I8 | Inlet | Front | Standard | Grille | Triple | G3 | 3.5 | 0.0003915 | -0.058238 | 30.4968 | 800 | 445.8407 |  | 650 | 322.2829 |  | 75 | 150.47 |  | 800 | 322.2829 | 800 | 264.7402 |  | 650 | 196.8959 |  | 75 | 84.9684 |  | 800 | 196.8959 | 800 | 394.3636 |  | 650 | 298.0618 |  | 75 | 150.47 |  | 800 | 298.0618 | 800 | 206.6929 |  | 650 | 158.0503 |  | 75 | 73.3956 |  | 800 | 158.0503
I8 | Inlet | Cup | Standard | Grille | Triple | G3 | 3.5 | 0.008403 | 0.20779 | 22.1172 | 810 | 454.9603 |  | 655 | 326.2631 |  | 77.5 | 158.3549 |  | 810 | 326.2631 | 810 | 270.5549 |  | 655 | 199.7333 |  | 77.5 | 88.6915 |  | 810 | 199.7333 | 810 | 402.1689 |  | 655 | 301.8186 |  | 77.5 | 158.3549 |  | 810 | 301.8186 | 810 | 211.1179 |  | 655 | 160.3136 |  | 77.5 | 76.4537 |  | 810 | 160.3136
[11 empty] | 820 | 464.1661 |  | 660 | 330.2661 |  | 80 | 166.4292 |  | 820 | 330.2661 | 820 | 276.4336 |  | 660 | 202.5947 |  | 80 | 92.5196 |  | 820 | 202.5947 | 820 | 410.0476 |  | 660 | 305.6012 |  | 80 | 166.4292 |  | 820 | 305.6012 | 820 | 215.5906 |  | 660 | 162.5966 |  | 80 | 79.6167 |  | 820 | 162.5966
[11 empty] | 830 | 473.4581 |  | 665 | 334.292 |  | 82.5 | 174.6927 |  | 830 | 334.292 | 830 | 282.3764 |  | 665 | 205.4801 |  | 82.5 | 96.4528 |  | 830 | 205.4801 | 830 | 417.9994 |  | 665 | 309.4097 |  | 82.5 | 174.6927 |  | 830 | 309.4097 | 830 | 220.111 |  | 665 | 164.899 |  | 82.5 | 82.8849 |  | 830 | 164.899
[11 empty] | 840 | 482.8364 |  | 670 | 338.3408 |  | 85 | 183.1457 |  | 840 | 338.3408 | 840 | 288.3832 |  | 670 | 208.3895 |  | 85 | 100.491 |  | 840 | 208.3895 | 840 | 426.0244 |  | 670 | 313.244 |  | 85 | 183.1457 |  | 840 | 313.244 | 840 | 224.679 |  | 670 | 167.2211 |  | 85 | 86.258 |  | 840 | 167.2211
[11 empty] | 850 | 492.301 |  | 675 | 342.4124 |  | 87.5 | 191.7879 |  | 850 | 342.4124 | 850 | 294.4541 |  | 675 | 211.3229 |  | 87.5 | 104.6343 |  | 850 | 211.3229 | 850 | 434.1227 |  | 675 | 317.1041 |  | 87.5 | 191.7879 |  | 850 | 317.1041 | 850 | 229.2946 |  | 675 | 169.5627 |  | 87.5 | 89.7362 |  | 850 | 169.5627
[11 empty] | 860 | 501.8517 |  | 680 | 346.507 |  | 90 | 200.6196 |  | 860 | 346.507 | 860 | 300.5891 |  | 680 | 214.2804 |  | 90 | 108.8826 |  | 860 | 214.2804 | 860 | 442.2942 |  | 680 | 320.99 |  | 90 | 200.6196 |  | 860 | 320.99 | 860 | 233.9578 |  | 680 | 171.924 |  | 90 | 93.3194 |  | 860 | 171.924
[11 empty] | 870 | 511.4887 |  | 685 | 350.6244 |  | 92.5 | 209.6405 |  | 870 | 350.6244 | 870 | 306.7881 |  | 685 | 217.2619 |  | 92.5 | 113.2359 |  | 870 | 217.2619 | 870 | 450.5389 |  | 685 | 324.9018 |  | 92.5 | 209.6405 |  | 870 | 324.9018 | 870 | 238.6687 |  | 685 | 174.3047 |  | 92.5 | 97.0077 |  | 870 | 174.3047
[11 empty] | 880 | 521.212 |  | 690 | 354.7646 |  | 95 | 218.8508 |  | 880 | 354.7646 | 880 | 313.0512 |  | 690 | 220.2673 |  | 95 | 117.6943 |  | 880 | 220.2673 | 880 | 458.8569 |  | 690 | 328.8394 |  | 95 | 218.8508 |  | 880 | 328.8394 | 880 | 243.4272 |  | 690 | 176.7051 |  | 95 | 100.801 |  | 880 | 176.7051
[11 empty] | 890 | 531.0214 |  | 695 | 358.9278 |  | 97.5 | 228.2505 |  | 890 | 358.9278 | 890 | 319.3783 |  | 695 | 223.2968 |  | 97.5 | 122.2577 |  | 890 | 223.2968 | 890 | 467.2481 |  | 695 | 332.8028 |  | 97.5 | 228.2505 |  | 890 | 332.8028 | 890 | 248.2334 |  | 695 | 179.125 |  | 97.5 | 104.6993 |  | 890 | 179.125
[11 empty] | 900 | 540.9171 |  | 700 | 363.1138 |  | 100 | 237.8395 |  | 900 | 363.1138 | 900 | 325.7695 |  | 700 | 226.3503 |  | 100 | 126.9262 |  | 900 | 226.3503 | 900 | 475.7125 |  | 700 | 336.792 |  | 100 | 237.8395 |  | 900 | 336.792 | 900 | 253.0871 |  | 700 | 181.5646 |  | 100 | 108.7027 |  | 900 | 181.5646

## New
[11 empty] | I1 | Single Inlet, G4 Filter |  | I2 | Triple Inlet, G4 Filter |  | I2 |  |  |  |  | I3 | Single Inlet, G3 Filter |  | I4 | Triple Inlet, G3 Filter |  | I4 |  |  |  |  | I5 | Single Inlet, G4 Filter, Grille |  | I6 | Triple Inlet, G4 Filter, Grille |  | I6 |  |  |  |  | I7 | Single Inlet, G3 Filter, Grille |  | I8 | Triple Inlet, G3 Filter, Grille |  | I8
| 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 0.00027333 | 0.066214 | 7.3395 | 0.00043044 | -0.055112 | 31.5468 | 0.0073882 | 0.22472 | 21.5406 |  |  | 0.00023678 | 0.02849 | 7.2948 | 0.00039473 | -0.093858 | 31.8141 | 0.0066 | 0.0769 | 21.717 |  |  | 0.0001912 | 0.059488 | 7.2371 | 0.00034167 | -0.054079 | 29.534 | 0.0073882 | 0.22472 | 21.5406 |  |  | 0.00015465 | 0.021764 | 7.1924 | 0.00030597 | -0.092825 | 29.8012 | 0.0065725 | 0.076861 | 21.7172
Number | Type | Entry Section Sub-type | Cross-sectional Area | Entry Geometry | Number of inlets | Filter | N_filter | a2 | a1 | a0 | Flowrate - [m^3/h] | Static Pressure - [Pa] |  | Flowrate - [m^3/h] | Static Pressure - [Pa] |  | Flowrate - [m^3/h] | Static Pressure - [Pa] |  | Flowrate - [m^3/h] | Static Pressure - [Pa] | Flowrate - [m^3/h] | Static Pressure - [Pa] |  | Flowrate - [m^3/h] | Static Pressure - [Pa] |  | Flowrate - [m^3/h] | Static Pressure - [Pa] |  | Flowrate - [m^3/h] | Static Pressure - [Pa] | Flowrate - [m^3/h] | Static Pressure - [Pa] |  | Flowrate - [m^3/h] | Static Pressure - [Pa] |  | Flowrate - [m^3/h] | Static Pressure - [Pa] |  | Flowrate - [m^3/h] | Static Pressure - [Pa] | Flowrate - [m^3/h] | Static Pressure - [Pa] |  | Flowrate - [m^3/h] | Static Pressure - [Pa] |  | Flowrate - [m^3/h] | Static Pressure - [Pa] |  | Flowrate - [m^3/h] | Static Pressure - [Pa]
I1 | Inlet | Front | Standard | Concealed | Single | G4 | 1 | 0.00027333 | 0.066214 | 7.3395 | 700 | 187.6232 |  | 600 | 153.4374 |  | 50 | 51.2472 |  | 700 | 153.4374 | 700 | 143.2589 |  | 600 | 117.603 |  | 50 | 42.062 |  | 700 | 117.603 | 700 | 142.5681 |  | 600 | 120.0881 |  | 50 | 51.2472 |  | 700 | 120.0881 | 700 | 98.2038 |  | 600 | 84.2537 |  | 50 | 41.9916 |  | 700 | 84.2537
I2 | Inlet | Front | Standard | Concealed | Triple | G4 | 1 | 0.00043044 | -0.055112 | 31.5468 | 710 | 192.1393 |  | 605 | 155.7552 |  | 52.5 | 53.7022 |  | 710 | 155.7552 | 710 | 146.8823 |  | 605 | 119.512 |  | 52.5 | 43.9455 |  | 710 | 119.512 | 710 | 145.8589 |  | 605 | 121.8763 |  | 52.5 | 53.7022 |  | 710 | 121.8763 | 710 | 100.6019 |  | 605 | 85.633 |  | 52.5 | 43.8679 |  | 710 | 85.633
I2 | Inlet | Cup | Standard | Concealed | Triple | G4 | 1 | 0.0073882 | 0.22472 | 21.5406 | 720 | 196.7102 |  | 610 | 158.0945 |  | 55 | 56.2496 |  | 720 | 158.0945 | 720 | 150.5532 |  | 610 | 121.4407 |  | 55 | 45.9115 |  | 720 | 121.4407 | 720 | 149.188 |  | 610 | 123.6815 |  | 55 | 56.2496 |  | 720 | 123.6815 | 720 | 103.031 |  | 610 | 87.0276 |  | 55 | 45.8264 |  | 720 | 87.0276
I3 | Inlet | Front | Standard | Concealed | Single | G3 | 1 | 0.00023678 | 0.02849 | 7.2948 | 730 | 201.3356 |  | 615 | 160.4554 |  | 57.5 | 58.8893 |  | 730 | 160.4554 | 730 | 154.2713 |  | 615 | 123.3891 |  | 57.5 | 47.96 |  | 730 | 123.3891 | 730 | 152.5554 |  | 615 | 125.5039 |  | 57.5 | 58.8893 |  | 730 | 125.5039 | 730 | 105.491 |  | 615 | 88.4376 |  | 57.5 | 47.8671 |  | 730 | 88.4376
I4 | Inlet | Front | Standard | Concealed | Triple | G3 | 1 | 0.00039473 | -0.093858 | 31.8141 | 740 | 206.0158 |  | 620 | 162.8378 |  | 60 | 61.6214 |  | 740 | 162.8378 | 740 | 158.0369 |  | 620 | 125.3573 |  | 60 | 50.091 |  | 740 | 125.3573 | 740 | 155.9609 |  | 620 | 127.3433 |  | 60 | 61.6214 |  | 740 | 127.3433 | 740 | 107.982 |  | 620 | 89.8628 |  | 60 | 49.99 |  | 740 | 89.8628
I4 | Inlet | Cup | Standard | Concealed | Triple | G3 | 1 | 0.0066 | 0.0769 | 21.717 | 750 | 210.7506 |  | 625 | 165.2417 |  | 62.5 | 64.4459 |  | 750 | 165.2417 | 750 | 161.8498 |  | 625 | 127.3452 |  | 62.5 | 52.3045 |  | 750 | 127.3452 | 750 | 159.4047 |  | 625 | 129.1998 |  | 62.5 | 64.4459 |  | 750 | 129.1998 | 750 | 110.5039 |  | 625 | 91.3033 |  | 62.5 | 52.1949 |  | 750 | 91.3033
I5 | Inlet | Front | Standard | Grille | Single | G4 | 1 | 0.0001912 | 0.059488 | 7.2371 | 760 | 215.5401 |  | 630 | 167.6672 |  | 65 | 67.3627 |  | 760 | 167.6672 | 760 | 165.71 |  | 630 | 129.3529 |  | 65 | 54.6005 |  | 760 | 129.3529 | 760 | 162.8868 |  | 630 | 131.0734 |  | 65 | 67.3627 |  | 760 | 131.0734 | 760 | 113.0567 |  | 630 | 92.7591 |  | 65 | 54.4821 |  | 760 | 92.7591
I6 | Inlet | Front | Standard | Grille | Triple | G4 | 1 | 0.00034167 | -0.054079 | 29.534 | 770 | 220.3843 |  | 635 | 170.1141 |  | 67.5 | 70.3718 |  | 770 | 170.1141 | 770 | 169.6176 |  | 635 | 131.3803 |  | 67.5 | 56.979 |  | 770 | 131.3803 | 770 | 166.4071 |  | 635 | 132.964 |  | 67.5 | 70.3718 |  | 770 | 132.964 | 770 | 115.6404 |  | 635 | 94.2302 |  | 67.5 | 56.8514 |  | 770 | 94.2302
I6 | Inlet | Cup | Standard | Grille | Triple | G4 | 1 | 0.0073882 | 0.22472 | 21.5406 | 780 | 225.2831 |  | 640 | 172.5826 |  | 70 | 73.4733 |  | 780 | 172.5826 | 780 | 173.5726 |  | 640 | 133.4274 |  | 70 | 59.44 |  | 780 | 133.4274 | 780 | 169.9656 |  | 640 | 134.8718 |  | 70 | 73.4733 |  | 780 | 134.8718 | 780 | 118.255 |  | 640 | 95.7166 |  | 70 | 59.3029 |  | 780 | 95.7166
I7 | Inlet | Front | Standard | Grille | Single | G3 | 1 | 0.00015465 | 0.021764 | 7.1924 | 790 | 230.2366 |  | 645 | 175.0726 |  | 72.5 | 76.6672 |  | 790 | 175.0726 | 790 | 177.5749 |  | 645 | 135.4943 |  | 72.5 | 61.9835 |  | 790 | 135.4943 | 790 | 173.5623 |  | 645 | 136.7966 |  | 72.5 | 76.6672 |  | 790 | 136.7966 | 790 | 120.9006 |  | 645 | 97.2183 |  | 72.5 | 61.8365 |  | 790 | 97.2183
I8 | Inlet | Front | Standard | Grille | Triple | G3 | 1 | 0.00030597 | -0.092825 | 29.8012 | 800 | 235.2448 |  | 650 | 177.5842 |  | 75 | 79.9534 |  | 800 | 177.5842 | 800 | 181.6246 |  | 650 | 137.5809 |  | 75 | 64.6095 |  | 800 | 137.5809 | 800 | 177.1974 |  | 650 | 138.7386 |  | 75 | 79.9534 |  | 800 | 138.7386 | 800 | 123.5772 |  | 650 | 98.7353 |  | 75 | 64.4522 |  | 800 | 98.7353
I8 | Inlet | Cup | Standard | Grille | Triple | G3 | 1 | 0.0065725 | 0.076861 | 21.7172 | 810 | 240.3076 |  | 655 | 180.1172 |  | 77.5 | 83.332 |  | 810 | 180.1172 | 810 | 185.7216 |  | 655 | 139.6872 |  | 77.5 | 67.318 |  | 810 | 139.6872 | 810 | 180.8706 |  | 655 | 140.6976 |  | 77.5 | 83.332 |  | 810 | 140.6976 | 810 | 126.2846 |  | 655 | 100.2676 |  | 77.5 | 67.1502 |  | 810 | 100.2676
[11 empty] | 820 | 245.4251 |  | 660 | 182.6718 |  | 80 | 86.8029 |  | 820 | 182.6718 | 820 | 189.866 |  | 660 | 141.8133 |  | 80 | 70.109 |  | 820 | 141.8133 | 820 | 184.5821 |  | 660 | 142.6737 |  | 80 | 86.8029 |  | 820 | 142.6737 | 820 | 129.023 |  | 660 | 101.8152 |  | 80 | 69.9303 |  | 820 | 101.8152
[11 empty] | 830 | 250.5972 |  | 665 | 185.2479 |  | 82.5 | 90.3662 |  | 830 | 185.2479 | 830 | 194.0577 |  | 665 | 143.9591 |  | 82.5 | 72.9825 |  | 830 | 143.9591 | 830 | 188.3318 |  | 665 | 144.6668 |  | 82.5 | 90.3662 |  | 830 | 144.6668 | 830 | 131.7923 |  | 665 | 103.3781 |  | 82.5 | 72.7925 |  | 830 | 103.3781
[11 empty] | 840 | 255.8241 |  | 670 | 187.8455 |  | 85 | 94.0218 |  | 840 | 187.8455 | 840 | 198.2968 |  | 670 | 146.1247 |  | 85 | 75.9385 |  | 840 | 146.1247 | 840 | 192.1198 |  | 670 | 146.6771 |  | 85 | 94.0218 |  | 840 | 146.6771 | 840 | 134.5925 |  | 670 | 104.9563 |  | 85 | 75.7369 |  | 840 | 104.9563
[11 empty] | 850 | 261.1056 |  | 675 | 190.4646 |  | 87.5 | 97.7698 |  | 850 | 190.4646 | 850 | 202.5832 |  | 675 | 148.31 |  | 87.5 | 78.977 |  | 850 | 148.31 | 850 | 195.946 |  | 675 | 148.7044 |  | 87.5 | 97.7698 |  | 850 | 148.7044 | 850 | 137.4237 |  | 675 | 106.5498 |  | 87.5 | 78.7634 |  | 850 | 106.5498
[11 empty] | 860 | 266.4417 |  | 680 | 193.1053 |  | 90 | 101.6101 |  | 860 | 193.1053 | 860 | 206.917 |  | 680 | 150.515 |  | 90 | 82.098 |  | 860 | 150.515 | 860 | 199.8105 |  | 680 | 150.7489 |  | 90 | 101.6101 |  | 860 | 150.7489 | 860 | 140.2858 |  | 680 | 108.1586 |  | 90 | 81.8722 |  | 860 | 108.1586
[11 empty] | 870 | 271.8325 |  | 685 | 195.7675 |  | 92.5 | 105.5428 |  | 870 | 195.7675 | 870 | 211.2982 |  | 685 | 152.7398 |  | 92.5 | 85.3015 |  | 870 | 152.7398 | 870 | 203.7132 |  | 685 | 152.8104 |  | 92.5 | 105.5428 |  | 870 | 152.8104 | 870 | 143.1788 |  | 685 | 109.7827 |  | 92.5 | 85.063 |  | 870 | 109.7827
[11 empty] | 880 | 277.278 |  | 690 | 198.4512 |  | 95 | 109.5678 |  | 880 | 198.4512 | 880 | 215.7267 |  | 690 | 154.9843 |  | 95 | 88.5875 |  | 880 | 154.9843 | 880 | 207.6541 |  | 690 | 154.889 |  | 95 | 109.5678 |  | 880 | 154.889 | 880 | 146.1028 |  | 690 | 111.422 |  | 95 | 88.336 |  | 880 | 111.422
[11 empty] | 890 | 282.7782 |  | 695 | 201.1564 |  | 97.5 | 113.6852 |  | 890 | 201.1564 | 890 | 220.2026 |  | 695 | 157.2485 |  | 97.5 | 91.956 |  | 890 | 157.2485 | 890 | 211.6333 |  | 695 | 156.9846 |  | 97.5 | 113.6852 |  | 890 | 156.9846 | 890 | 149.0576 |  | 695 | 113.0767 |  | 97.5 | 91.6912 |  | 890 | 113.0767
[11 empty] | 900 | 288.333 |  | 700 | 203.8832 |  | 100 | 117.895 |  | 900 | 203.8832 | 900 | 224.7258 |  | 700 | 159.5325 |  | 100 | 95.407 |  | 900 | 159.5325 | 900 | 215.6507 |  | 700 | 159.0974 |  | 100 | 117.895 |  | 900 | 159.0974 | 900 | 152.0435 |  | 700 | 114.7467 |  | 100 | 95.1286 |  | 900 | 114.7467