## Pressure Loss Curves
Number | Type | Entry Section Sub-type | Cross-sectional Area | Entry Geometry | Number of inlets | Filter | N_filter | Fan Array Details | a2 | a1 | a0
I1 | Inlet | Front | Standard | Concealed | Single | G4 | 3.5 | 3 fans of φ160 and W=51 | 0.00043117 | 0.21778 | -4.3294
I2 | Inlet | Front | Standard | Concealed | Triple | G4 | 3.5 | 3 fans of φ160 and W=51 | 0.0004575 | 0.19899 | -0.35482
I2 | Inlet | Cup | Standard | Concealed | Triple | G4 | 3.5 | 3 fans of φ160 and W=51 | 0.015148 | 0.84394 | 1.9692
I3 | Inlet | Front | Standard | Concealed | Single | G3 | 3.5 | 3 fans of φ160 and W=51 | 0.0003203 | 0.065787 | 7.1203
I4 | Inlet | Front | Standard | Concealed | Triple | G3 | 3.5 | 3 fans of φ160 and W=51 | 0.00048027 | -0.059271 | 32.5097
I4 | Inlet | Cup | Standard | Concealed | Triple | G3 | 3.5 | 3 fans of φ160 and W=51 | 0.008403 | 0.20779 | 22.1172
I5 | Inlet | Front | Standard | Grille | Single | G4 | 3.5 | 3 fans of φ160 and W=51 | 0.00036611 | 0.1911 | 7.1744
I6 | Inlet | Front | Standard | Grille | Triple | G4 | 3.5 | 3 fans of φ160 and W=51 | 0.00051647 | 0.077373 | 29.5615
I6 | Inlet | Cup | Standard | Grille | Triple | G4 | 3.5 | 3 fans of φ160 and W=51 | 0.015148 | 0.84394 | 1.9692
I7 | Inlet | Front | Standard | Grille | Single | G3 | 3.5 | 3 fans of φ160 and W=51 | 0.00023817 | 0.059061 | 7.0179
I8 | Inlet | Front | Standard | Grille | Triple | G3 | 3.5 | 3 fans of φ160 and W=51 | 0.0003915 | -0.058238 | 30.4968
I8 | Inlet | Cup | Standard | Grille | Triple | G3 | 3.5 | 3 fans of φ160 and W=51 | 0.008403 | 0.20779 | 22.1172
I1 | Inlet | Front | Standard | Concealed | Single | G4 | 1 | 3 fans of φ160 and W=51 | 0.00027333 | 0.066214 | 7.3395
I2 | Inlet | Front | Standard | Concealed | Triple | G4 | 1 | 3 fans of φ160 and W=51 | 0.00043044 | -0.055112 | 31.5468
I2 | Inlet | Cup | Standard | Concealed | Triple | G4 | 1 | 3 fans of φ160 and W=51 | 0.0073882 | 0.22472 | 21.5406
I3 | Inlet | Front | Standard | Concealed | Single | G3 | 1 | 3 fans of φ160 and W=51 | 0.00023678 | 0.02849 | 7.2948
I4 | Inlet | Front | Standard | Concealed | Triple | G3 | 1 | 3 fans of φ160 and W=51 | 0.00039473 | -0.093858 | 31.8141
I4 | Inlet | Cup | Standard | Concealed | Triple | G3 | 1 | 3 fans of φ160 and W=51 | 0.0066 | 0.0769 | 21.717
I5 | Inlet | Front | Standard | Grille | Single | G4 | 1 | 3 fans of φ160 and W=51 | 0.0001912 | 0.059488 | 7.2371
I6 | Inlet | Front | Standard | Grille | Triple | G4 | 1 | 3 fans of φ160 and W=51 | 0.00034167 | -0.054079 | 29.534
I6 | Inlet | Cup | Standard | Grille | Triple | G4 | 1 | 3 fans of φ160 and W=51 | 0.0073882 | 0.22472 | 21.5406
I7 | Inlet | Front | Standard | Grille | Single | G3 | 1 | 3 fans of φ160 and W=51 | 0.00015465 | 0.021764 | 7.1924
I8 | Inlet | Front | Standard | Grille | Triple | G3 | 1 | 3 fans of φ160 and W=51 | 0.00030597 | -0.092825 | 29.8012
I8 | Inlet | Cup | Standard | Grille | Triple | G3 | 1 | 3 fans of φ160 and W=51 | 0.0065725 | 0.076861 | 21.7172
O1 | Outlet | Back | Standard | Concealed | Single | G4 | 3.5 | 3 fans of φ160 and W=51 | 0.00043117 | 0.21778 | -4.3294
O2 | Outlet | Back | Standard | Concealed | Single | G3 | 3.5 | 3 fans of φ160 and W=51 | 0.0003203 | 0.065787 | 7.1203
O3 | Outlet | Back | Increased 01 | Concealed | Single | G4 | 3.5 | 3 fans of φ160 and W=51 | 0.0003 | 0.1564 | 2.9753
O4 | Outlet | Back | Increased 01 | Concealed | Single | G3 | 3.5 | 3 fans of φ160 and W=51 | 0.0003 | 0.0344 | 4.7606
O5 | Outlet | Back | Standard | Grille | Single | G4 | 3.5 | 3 fans of φ160 and W=51 | 0.00036611 | 0.1911 | 7.1744
O6 | Outlet | Back | Standard | Grille | Single | G3 | 3.5 | 3 fans of φ160 and W=51 | 0.00023817 | 0.059061 | 7.0179
O7 | Outlet | Back | Increased 01 | Grille | Single | G4 | 3.5 | 3 fans of φ160 and W=51 | 0.0002 | 0.1456 | 5.5894
O8 | Outlet | Back | Increased 01 | Grille | Single | G3 | 3.5 | 3 fans of φ160 and W=51 | 0.0002 | 0.0391 | 4.1146
O9 | Outlet | Back | Standard | Concealed | Single | G4 | 1 | 3 fans of φ160 and W=51 | 0.00027333 | 0.066214 | 7.3395
O2 | Outlet | Back | Standard | Concealed | Single | G3 | 1 | 3 fans of φ160 and W=51 | 0.00023678 | 0.02849 | 7.2948
O3 | Outlet | Back | Increased 01 | Concealed | Single | G4 | 1 | 3 fans of φ160 and W=51 | 0.0003 | 0.0145 | 11.192
O4 | Outlet | Back | Increased 01 | Concealed | Single | G3 | 1 | 3 fans of φ160 and W=51 | 0.0002 | 0.0005 | 5.1402
O5 | Outlet | Back | Standard | Grille | Single | G4 | 1 | 3 fans of φ160 and W=51 | 0.0001912 | 0.059488 | 7.2371
O6 | Outlet | Back | Standard | Grille | Single | G3 | 1 | 3 fans of φ160 and W=51 | 0.00015465 | 0.021764 | 7.1924
O7 | Outlet | Back | Increased 01 | Grille | Single | G4 | 1 | 3 fans of φ160 and W=51 | 0.0001 | 0.0356 | 4.9156
O8 | Outlet | Back | Increased 01 | Grille | Single | G3 | 1 | 3 fans of φ160 and W=51 | 0.0001 | 0.0052 | 4.4943
I9 | Inlet | Front | Standard | Concealed | Single | G4 | 3.5 | 14 fans of φ60 and W=76 | 0.00035535 | 0.19613 | -1.4263
O9 | Outlet | Back | Increased 01 | Concealed | Single | G3 | 3.5 | 10 fans of φ60 and W=76 | 0.00026313 | 0.086026 | -13.0257
I10 | Inlet | Front | Standard | Concealed | Single | G4 | 1 | 14 fans of φ60 and W=76 | 0.00011752 | 0.17135 | -37.6211
O10 | Outlet | Back | Increased 01 | Concealed | Single | G3 | 1 | 10 fans of φ60 and W=76 | 0.0002047 | 0.030906 | -6.575
HMI1 | Internal | Non-applicable | LCD | Non-applicable | 4 Inlets | Non-applicable | 1 | 4 fans inlet / 4 fans outlet | 0.001037 | -0.10178 | 10.7486
PCP | Internal | Non-applicable | PCP_Min | Non-applicable | 4 Inlets | Non-applicable | 1 | Minimum Pressure Loss | 0.0002359 | 0.080052 | 1.6766
PCP | Internal | Non-applicable | PCP_Max | Non-applicable | 4 Inlets | Non-applicable | 1 | Maximum Pressure Loss | 0.00080857 | -0.018815 | 12.9036
PCE | Internal | Non-applicable | PCE_Min | Non-applicable | 3 Inlets | Non-applicable | 1 | Minimum Pressure Loss | 0.00065301 | 0.066441 | -1.778
PCE | Internal | Non-applicable | PCE_Max | Non-applicable | 3 Inlets | Non-applicable | 1 | Maximum Pressure Loss | 0.0032955 | 0.012062 | 0.041091
I11 | Inlet | Front | Standard | Concealed | Single | G3 | 3.5 | 14 fans of φ60 and W=76 | 0.00015416 | 0.17843 | -39.9378
I12 | Inlet | Front | Standard | Concealed | Single | G3 | 1 | 14 fans of φ60 and W=76 | 6.2697e-05 | 0.16165 | -42.9656
I13 | Inlet | Front | Standard | Concealed | Single | G3 | 3.5 | 11 fans of φ60 and W=38 | 0.0002804 | 0.083856 | -9.8397
I14 | Inlet | Front | Standard | Concealed | Single | G3 | 1 | 11 fans of φ60 and W=38 | 0.00016726 | 0.019293 | 14.3119